## Introduction
Introduction
A key factor in building heat gain and loss may be the infiltration rate, or the rate at which outdoor air is exchanged with conditioned interior air through the envelope. This spreadsheet tool outlines a set of simplified equations aimed at converting typical, real world infiltration measurements into metrics that can be input into EnergyPlus.
In using methods outlined in the document Infiltration Modeling Guidelines for Commercial Building Energy Analysis by the Pacific Northwest National Laboratory, we were able to convert common metrics of I75 and ACH50, into ones that could be conveniently input into an Energy Plus Model (Idesign and ACHnat).
KEY DEFINITIONS
ACH50-The number of complete air changes that occur within an hour when the building is pressurized at 50 Pascals. This metric is usually used in residential infiltration measurement.
ACHnat-The number of natural air changes that occur with an hour when the building is naturally pressurized.
I75- The infiltration flow rate of air in cubic feet per minute per square foot of exterior exposed surface area when the building is pressurized at 75 Pascals. This metric is more commonly used in commercial infiltration measurement.
Idesign- The infiltration flow rate of air in cubic feet per minute per square foot of exterior exposed surface area when the building is naturally pressurized.
SPREADSHEETS
Spreadsheets 1 and 2 can be used to convert I75 into Idesign. Spreadsheet "1. I75 to Idesign Text," explains the method and equations for the conversion. "2. I75 to Idesign Calculations," is an interactive spreadsheet that takes your project's input and provides an output that can be used in EnergyPlus.
Spreadsheets 3 and 4 can be used to convert ACH50 into ACHnat. As in spreadsheets 1-2, "3. ACH50 to ACHnat Text," explains the method and equations for the conversion. "4. ACH50 to ACHnat Calculations," is an interactive spreadsheet that takes your project's input and provides an output that can be used in EnergyPlus.
Spreadsheets 5 and 6 are for comparing ACH50 into Idesign metrics. As in spreadsheets 1-4, "5. Compare ACH and I Text," explains the method and equations for the conversion. "6. Compare ACH to I Calculation," is an interactive spreadsheet that takes your project's input and provides an output of comparisions between the diffferent metrics
Spreadsheet 7 is a provides a reverse calculation. "7. Reverse Calcs" allows you to convert from an EnergyPlus input into I75.
Spreadsheet 8 is a reference tab. "8. Appendix" contains useful reference charts for spreadsheets 1-7.
NOTE: At this time, this calculation tool does not take into account infiltration from stack pressure, only horizontal wind pressure.

## 1. I75 to Idesign Text
Converting I75 to Idesign Method Explaination
Commercial infiltration rates are often measured in cubic feet per minute per square foot of exterior surface area when the building is pressurized at 75 Pascals (or I75). The corresponding input for Energy Plus, however, is cubic meters per second per square meters of exterior surface area when the building is naturally pressurized (or Idesign). The spreadsheet calculation tool on the the tab "I75 to Idesign Calculations" has been created by the IDL that follows the following conversion steps.
In order to convert metrics, we need the following information:
1. Infiltration rate in I75,
2. Terrain factors for the building site and weather station site
| 1 | Infiltration Rate in I75
If the desired infiltration rate is in imperial metrics of CFM/f2, it will need to be converted to (m3/s)/m2 prior to entering it into the text equation at the bottom of this sheet. This can be done using the conversion equation below. However, there has been an equation added on the following spreadsheet that allows an imperial input as well.
Xm3/sec/m2 = X*((CFM*0.000472m3/sec)/(f2*0.0902903m2)) = X*(0.000472/0.09290304) = X*0.00508
| 2 | Terrain Factors
The two terrain factors of α and δ are included to account for wind velocity changes due to obstacles such as other buildings and trees. Typical values are outlined in Chart 1 in the "Appendix" tab; factors for both the building site and weather station site were chosen based on characteristics that best fit with those described in the leftmost column.
CONVERTING I75 to Idesign
Once the infiltration rate and terrain factors have been gathered and calculated, the following equation can be used to convert I75 to Idesign:
Idesign=(αbldg+1)*(I75(.5Cs*ρ*UH2/75)n
where:
Idesign is the infiltration rate in m3/sec/m2,
αbldg is the terrain factor of the building from Chart 1 in the "Appendix" tab,
Cs is the average wind pressure coefficient (calculated average of 0.1617)
ρ is the pressure of air (1.18 kg/m3),
UH is the wind speed at the top of the building (assumed to be 4.47 m/s), and
n is the flow exponent (0.65).
Each of the constants were obtained from methods outlined in the document Infiltration Modeling Guidelines for Commercial Building Energy Analysis. The resulting Idesign factor can now be used in the Energy Plus model; it should be plugged it into the infiltration object as Flow/ExteriorArea.

## 2. I75 to Idesign Calculations
Converting I75 to Idesign Calculation Spreadsheet
Enter values in into the grey cells. Outputs will be in the yellow cells.
| You will need the following information: |  | How to get this information:
| 1. Infiltration rate in I75 |  | 1. Use I75 obtained from measurement in a blower door test OR use typical researched value (for example national building stock average of 1.8 I75); see Chart 4 in the "Appendix" tab
| 2. Terrain factors for the building site and weather station site |  | 2. See Chart 1 in the "Appendix" tab and choose the best fitting site conditions for both the building and weather station sites.
CONVERTING I75 TO Idesign
| Which units would you like to INPUT?: |  | Metric
Idesign=(αbldg+1)*(I75pa(.5Cs*p*Uh2/75)n
| I75 | infiltration rate at 75 pascals | 2000 | m3/s/m2 | Idesign | 209.5367 | m3/s/m2
| αbldg | (see chart 1 in "Appendix" tab) | 0.14
| UH | Wind speed at top of building | 4.47 | m2/s
| Cs | average wind pressure coefficient (Swami & Chandra) | 0.1617 |  |  | The above m3/s/m2 value would be entered into an EnergyPlus model under the Infiltration object and as Flow/ExteriorArea units.
| ρ | pressure of air | 1.18 | kg/m3
| n | flow exponent | 0.65

## 3. ACH50 to ACHnat Text
Converting ACH50 to ACH50 Method Explaination
Residential houses are more likely to use the metric of air changes per hour at 50 Pascals in measuring infiltration (or ACH50). Energy Plus input does not account for pressurization but uses the ACHnat metric, which is defined as the air changes per hour when the building is naturally pressurized. The spreadsheet calculation tool on the the tab "4. ACH50 to ACHnat Calculations" has been created by the IDL that follows the following conversion steps.
CONVERT ACH50 TO ACH50
In order to convert from ACH50 to ACHnat, we need the following information:
1. Infiltration rate in ACH50 and
2. the LBL factor of the site.
The LBL factor is based on the building height and location. It can be found based on the map developed by the Department of Energy (see Chart 2 in the "Appendix"tab). Once the LBL factor is found, we can plug it into the following equation to get the ACHnat rate:
ACHnat=ACH550/LBL Factor
The resulting ACHnat can be used in the Energy Plus model; it should be plugged into the infiltration object as AirChanges/Hour.

## 4.ACH50 to ACHnat Calculations
Converting ACH50 to ACHnat Calculation Spreadsheet
Enter values in into the grey cells. Outputs will be in the yellow cells.
| You will need the following information: |  |  | How to get this information:
| 1. ACH50 |  |  | 1. Use measurements obtained from a blower door test OR use typical researched value for estimation; see Chart 3 in "Appendix" tab for a good resource.
| 2. LBL Factor |  |  | 4. Use the map and Chart 2 in "Appendix" tab
ACH50 to ACHnat
ACHnat=ACH50/LBL Factor
| LBL Factor based on height and location | 10 |  | Air changes per hour at natural pressure | 1.55 | ACHnat
| Air changes per hour when pressurized at 50 Pa | 15.5 | ACH50 | The above ACHnat rate can be plugged into EnergyPlus in the Infiltration object as AirChanges/Hour

## 5. Compare ACH and I Text
Comparing ACH50 to Idesign and I75 Method Explaination
It may be helpful, as in the case of a small commercial building or a large residential building, to juxtapose the common metrics of both residential and commercial infiltration. This section provides simplified equations that can be used to convert I75 to ACH50 and vice versa. The spreadsheet calculation tool on the the tab "5. Compare ACH and I Calculation" has been created by the IDL that follows the following conversion steps.
In order to compare the two metrics, we need the following measurements:
1. I75 or ACH50 infiltration rate,
2. above grade exposed surface area (sum all exposed wall and roof area) in square feet
3. building volume in cubic feet,
4. LBL Factor,
5. terrain factor of building site.
The following equations use the same assumptions for each variable as previous defined.
CONVERTING I75 to ACH50
Step1: Convert I75 to Idesign
Use equations from "I75 to Idesign" tabs.
Step 2: Convert Idesign to CFMnat
CFMnat = Idesign *above grade surface area
where Idesign is the CFM/f2 rate obtained in Step 1, CFMnat is the flow rate in cubic feet per minute, and surface area is measured in square feet.
Step 3: Convert CFMnat to ACHnat
ACHnat=(CFMnat * 60 minutes)/ building volume
where building volume is measured in cubic feet.
Step 4: Convert ACHnat to ACH50
ACH50=ACHnat*LBL Factor
where the LBL Factor is based on building height and location and is obtained from the Energy Star Home Sealing Specification (See Chart 2 in the "Appendix" tab).
The resulting value is in air changes per hour when the building is pressurized at 50 Pascals, a metric that is typical for residential infiltration measurement.
CONVERTING ACH50 to I75
The previous steps are run in reverse to convert I75 to ACH50:
Step 1: Convert ACH50 to ACHnat
ACHnat=ACH50/LBL Factor
where the LBL Factor is based on location and is obtained from the Department of Energy’s Insulation Tables and LBL Conversion Factor Table (See Chart 2 in the "Appendix" tab).
Step 2: Convert ACHnat to CFMnat
CFMnat=(ACHnat /building volume)* 60 minutes
where ACHnat is the number of air changes per hour when the building is naturally pressurized and the building volume is measured in cubic feet.
Step 3: Convert CFMnat to Idesign
Idesign =(CFMnat/above grade surface area)
where the CFMnat is the flow rate in cubic feet per minute and above grade surface area is measured in feet squared.
Step 4: Convert Idesign metrics of CFM/f2 to m2/sec/m2
I75 (m2/sec/m2)= I75 (CFM/f2) * 0.00508
Step 5: Convert Idesign to I75
I75=(Idesign)/(αbldg+1)/(.5Cs*p*UH^2/75)n
where:
Idesign is the infiltration rate in m3/sec/m2,
αbldg is the terrain factor of the building from (See Chart 1 in the "Appendix" tab),
Cs is the average wind pressure coefficient (calculated average of 0.1617)
ρ is the pressure of air (1.18 kg/m3),
UH is the wind speed at the top of the building, and
n is the flow exponent (0.65).
To convert back into imperial units, use the equation below:
Idesign (CFM/f2)= Idesign (m2/sec/m2) / 0.00508
The resulting value is in cubic feet per minute per square foot of exterior surface area, a metric common to commercial infiltration measurement.

## 6.Compare ACH and I Calculation
Converting and Comparing ACH50 to Idesign Calculation Spreadsheet
Enter values in into the grey cells. Outputs will be in the yellow cells.
| You will need the following information: |  |  |  | How to get this information:
| 1. ACH50 OR I75 infiltration rate |  |  |  | 1. Use measurements obtained from a blower door test OR use typical researched value (for example national building stock average of 1.8 I75) See Charts 3 and 4 in "Appendix" tab for some typical values.
| 2. Above grade exposed surface area (sum all exposed wall and roof area) in square feet |  |  |  | 2. Use building construction drawings/models or take measurements at the building of all exposed area to the exterior environment.
| 3. Building volume in cubic feet |  |  |  | 3. Use building construciton drawings/models and multiply the building area by the ceiling height.
| 4. LBL Factor |  |  |  | 4. Use the map and Chart 2 in "Appendix" tab
| 5. Terrain factor of building site |  |  |  | 6. See Chart 1 in "Appendix" tab
| INPUTS: | [5 empty] | CONVERSION REFERENCES
[7 empty] | m3/s/m2 |  | = | cfm/f2 | 0
|  | Input Units: |  | Standard |  |  | cfm/f2 |  |  | m3/s/m2 | 0
|  | METHOD: |  | 1. ACH50 to I75
[7 empty] | m2 | 2 | = | ft2 | 21.5278
|  |  | Infiltation | 15.5 | ACH50 |  | ft2 |  | = | m2 | 0
|  |  | Above grade surface area | 10000 | ft2
|  |  | Building Volume | 50000 | ft3 |  | m3 |  | = | ft3 | 0
|  |  | LBL | 10 |  |  | ft3 |  | = | m3 | 0
|  |  | αbldg | 0.14
| METHOD 1: COMPARE/CONVERT ACH50 to I75 and Idesign | [5 empty] | METHOD 2: COMPARE/CONVERT I75 AND Idesignto ACH50
| Step 1: ACH50 to ACHnat | [5 empty] | Step 1: I75 to Inat
| ACHnat=ACH50/LBL Factor | [5 empty] | Idesign=(αbldg+1)*(I75pa(.5Cs*p*Uh^2/75)n
| LBL Factor based on chart | 10 |  | Air changes per hour at natural pressure | 1.55 | ACHnat | Flow rate when pressurized at 75 Pa | 0 | I75 | I75Flow rate per surface area when pressurized at 75 Pa | 0 | cfm/f2 I75
| Air changes per hour when pressurized at 50 Pa | 15.5 | ACH50 | The above ACHnat rate can be plugged into EnergyPlus in the Infiltration object as AirChanges/Hour |  |  | αbldg | 0.14 |  | Idesign Flow rate per surface area when naturally pressurized | 0 | m3/s/m2
[7 empty] | UH wind speed at building height | 10 | mph
[7 empty] | Cs | 0.1617 |  | The above m3/s/m2 value would be entered into an EnergyPlus model under the Infiltration object and as Flow/ExteriorArea units.
| Step 2: ACHnat to CFMnat | [5 empty] | ρ | 0.07363 | lb/ft2
[7 empty] | n | 0.65
CFM=(ACH*Building Volume)/60 minutes
| Building volume | 50000 | ft3 | Flow rate in cubic feet per minute | 1291.6667 | CFM | Step 2: Inat to CFMnat
| Air changes per hour at natural pressure | 1.55 | ACHnat
CFM=Inat*above grade surface area
| Step 3: CFMnat to Inat | [5 empty] | Above grade surface area | 10000 | f2 | Flow rate in cubic feet per minute | 0 | CFM
[7 empty] | Inat Flow rate at natural pressure | 0 | cfm/f2 I75
Inat=CFM/above grade surface area
| Above grade surface area | 10000 | f2 | Idesign Flow rate per surface area when naturally pressurized | 0.12917 | CFM/f2 | Step 3: CFMnat to ACHnat
| Flow rate in cubic feet per minute | 1291.6667 | CFM
ACH=(CFM*60 minute)/Building Volume
| Step 4: Idesign to I75 | [5 empty] | Building Volume | 50000 | ft3 | Air changes per hour at natural pressure | 0 | ACHnat
[7 empty] | Flow rate in cubic feet per minute | 0 | CFM | The above ACHnat rate can be plugged into EnergyPlus in the Infiltration object as AirChanges/Hour
I75=(Idesign)/(αbldg+1)/(.5Cs*p*Uh^2/75)n
| Idesign Flow rate per surface area when naturally pressurized | 0.12917 | CFM/f2 |  |  |  | Step 4: ACHnat to ACH50
| αbldg | 0.14 |  | I75Flow rate per surface area when pressurized at 75 Pa | 1.2327 | cfm/f2 I75
| UH wind speed at building height | 10 | mph | Idesign Flow rate per surface area when naturally pressurized | 0.00065617 | m3/s/m2 | ACH50=ACHnat*LBL Factor
| Cs | 0.1617 |  | The above m3/s/m2 value would be entered into an EnergyPlus model under the Infiltration object and as Flow/ExteriorArea units.
| ρ | 0.07363 | lb/ft2 |  |  |  | LBL Factor based on chart | 10 |  | Air changes per hour when pressurized at 50 Pa | 0 | ACH50
| n | 0.65 |  |  |  |  | Air changes per hour at natural pressure | 0 | ACHnat
| RESULTS: | [5 empty] | Results:
| 1. The Idesign value that can be plugged into EnergyPlus in the Infiltration object as Flow/Exterior Area is: |  |  |  | 0.00065617 | Idesign | 1. The Idesign value that can be plugged into EnergyPlus in the Infiltration object as Flow/Exterior Area is: |  |  |  | 0 | Idesign
| 2. The ACHnat value that can be plugged into EnergyPlus in the Infiltration object as AirChanges/Hour is: |  |  |  | 1.55 | ACHnat | 2. The ACHnat value that can be plugged into EnergyPlus in the Infiltration object as AirChanges/Hour is: |  |  |  | 0 | ACHnat
| 3. In this locaiton and for this building, | 15.5 | ACH50 | can be equated to approximately | 1.2327 | cfm/ft2 I75 | 3. In this locaiton and for this building, | 0 | cfm/ft2 I75 | can be equated to approximately | 0 | ACH50
| 4. In this locaiton and for this building, | 1.55 | ACHnat | can be equated to approximately | 0.00065617 | m3/s/m2 Idesign | 4. In this locaiton and for this building, | 0 | m3/s/m2 Idesign | can be equated to approximately | 0 | ACHnat
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Consider letting this page pull numbers from earlier pages

## 7. Reverse Calcs
Converting Idesign to I75
Enter values in into the grey cells. Outputs will be in the yellow cells.
| You will need the following information: |  | How to get this information:
| 1. Infiltration rate in Idesign |  | 1. Use Idesign that was input into EnergyPlus model.
| 2. Terrain factors for the building site and weather station site |  | 2. See Chart 1 in the "Appendix" tab and choose the best fitting site conditions for both the building and weather station sites.
CONVERTING I75 TO Idesign
| Which units would you like to OUTPUT?: |  | Metric
I75=(Idesign)/(αbldg+1)/(.5Cs*p*Uh^2/75)n
| Idesign | infiltration rate at natural pressure (from E+) | 209.5367 | m3/s/m2 | I75 | 2000 | m3/s/m2
| αbldg | (see chart 1 in "Appendix" tab) | 0.14
| UH | Wind speed at top of building | 4.47 | m3/s
| Cs | average wind pressure coefficient (Swami & Chandra) | 0.1617
| ρ | pressure of air | 1.18 | kg/m3
| n | flow exponent | 0.65

## 8. Appendix
APPENDIX
| CHART 1: Variables based on Terrain |  |  | CHART 2: LBL Factors Based on Location and number of stories | CHART 3: NIST researched statistics of infiltration of HOUSES | [5 empty] | References
| Terrain Characteristics | α | δ | [7 empty] | CONVERSION REFERENCES
| Category 1 |  |  |  |  | House Air Changes Per Hour |  |  |  |  | m3/s/m2 | = | cfm/f2 | 0
| Large city centres, in which at least 50% of buildings are higher than 21 m, over a distance of at least 2000 meters upwind | 0.33 | 460 |  |  |  | ACH50 | Construction Type |  |  | cfm/f2 |  | m3/s/m2 | 0
[7 empty] | 2 | Tight
[7 empty] | 5 | Moderately Tight |  |  | m2 | = | ft2 | 0
[7 empty] | 10 | Typical |  |  | ft2 | = | m2 | 0
| Category 2 | [5 empty] | >20 | Very Leaky
| Urban, suburban, wooded areas, and other areas with closely spaced obstructions compared to or larger than single-family dwellings (over a distance of at least 2000 meters upwind) | 0.22 | 370 |  |  |  | Based on US data from ASHRAE 1997 |  |  |  | m3 | = | ft3 | 0
[11 empty] | ft3 | = | m3 | 0
Source: Persily, A.K. (1998). Airtightness of Commercial and Institutional Buildings: Blowing Holes in the Myth of TightBuildings. Preceedings of Thermal Performance of the Exterior Envelopes of Buildings VII, pp. 829-837.
Category 3
| Open terrain with scattered obstacles generally less than 10 meters height | 0.14 | 270 |  | CHART 4: NIST researched statistics of infiltration of COMMERCIAL/INSTITUTIONAL BUILDINGS
Category 4
| Flat, unobstructed areas exposed to wind flowing over a large water body (no more than 500 meters inland) | 0.1 | 210
[8 empty] | m3/hr-m2 | 0 | cfm/f2
Source: Persily, A.K. (1998). Airtightness of Commercial and Institutional Buildings: Blowing Holes in the Myth of TightBuildings. Preceedings of Thermal Performance of the Exterior Envelopes of Buildings VII, pp. 829-837.
Source: Department of Energy (2001). Energy Star Home Sealing Specification
https://www.energystar.gov/ia/home_improvement/home_sealing/ES_HS_Spec_v1_0b.pdf